## config
STUDY CONFIGURATION
OLR FILE | C:\Program Files (x86)\ASPEN\1LPFv15\SAMPLE30.OLR
Study Branch | NEVADA | 132 | CLAYTOR | 132 | 1 | L
Fault Location | CLOSEIN | INT_10_15 | INT_10_15_EOP
Fault Type | 3PH | 1LG_A | 1LG_B
Outage (bus;tier) | CLAYTOR | 132 | 1
Outage Type | Single
Fault Z(R;X from/to/steps Ohm) | 0 | 0 | 1 | 1 | 1
Relay Group | CLAYTOR | 132 | NEVADA | 132 | 1 | L
Relay | CLPhase2 | CL-G1 | CL-G2
Relay Group | NEVADA | 132 | CLAYTOR | 132 | 10 | L
Relay | GCXTEST | GCXTEST2
#Relay | CLPhase2
BRANCH OUTAGES
1 | CLAYTOR | 132 | FIELDALE | 132 | 1 | L
2 | CLAYTOR | 132 | TENNESSEE | 132 | 1 | L
3 | CLAYTOR | 132 | GLEN LYN | 132 | 2 | L
4 | NEVADA | 132 | BUS0 | 132 | 1 | L
5 | NEVADA | 132 | REUSENS | 132 | 1 | L
6 | NEVADA | 132 | OHIO | 132 | 1 | L
7 | NEVADA | 132 | NEW HAMPSHR | 33 | 1 | X
8 | NEVADA | 132 | NEW HAMPSHR | 33 | 1 | T
9 | FIELDALE | 132 | OHIO | 132 | 1 | L
10 | TENNESSEE | 132 | TEXAS | 132 | 1 | L
11 | TENNESSEE | 132 | NEVADA | 132 | 1 | P
12 | TENNESSEE | 132 | VERMONT | 33 | 1 | T
13 | GLEN LYN | 132 | TEXAS | 132 | 1 | L
FAULTS DESCRIPTION | DESC | [PREFV VPF GENZTYPE IGNORE GENILIMIT VCCS MOV MOVITERF MINZMUPAIR MVASTYLE] | FLTSPCVS
1 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
2 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1'
3 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1'
4 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2'
5 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1'
6 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1'
7 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1'
8 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1'
9 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1'
10 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1'
11 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1'
12 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1'
13 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1'
14 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1'
15 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
16 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
17 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
18 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
19 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
20 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
21 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
22 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
23 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
24 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
25 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
26 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
27 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
28 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
29 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
30 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
31 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
32 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
33 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
34 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
35 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
36 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
37 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
38 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
39 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
40 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
41 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
42 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
43 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
44 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
45 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
46 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
47 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
48 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
49 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
50 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
51 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
52 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
53 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
54 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
55 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
56 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 10.00% with end opened Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1' ' ' 0 0 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
57 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
58 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
59 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
60 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
61 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
62 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
63 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
64 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
65 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
66 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
67 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
68 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
69 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
70 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 3LG 15.00% with end opened Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1' ' ' 0 0 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
71 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
72 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1'
73 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1'
74 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2'
75 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1'
76 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1'
77 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1'
78 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1'
79 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1'
80 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1'
81 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1'
82 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1'
83 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1'
84 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=A Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1'
85 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
86 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
87 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
88 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
89 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
90 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
91 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
92 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
93 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
94 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
95 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
96 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
97 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
98 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
99 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
100 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
101 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
102 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
103 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
104 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
105 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
106 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
107 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
108 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
109 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
110 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
111 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
112 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
113 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
114 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
115 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
116 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
117 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
118 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
119 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
120 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
121 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
122 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
123 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
124 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
125 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
126 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=A with end opened Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1' ' ' 0 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
127 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
128 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
129 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
130 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
131 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
132 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
133 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
134 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
135 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
136 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
137 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
138 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
139 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
140 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=A with end opened Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1' ' ' 0 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
141 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
142 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1'
143 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1'
144 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2'
145 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1'
146 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1'
147 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1'
148 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1'
149 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1'
150 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1'
151 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1'
152 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1'
153 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1'
154 | Close-In Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG Type=B Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 1 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1'
155 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
156 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
157 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
158 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
159 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
160 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
161 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
162 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
163 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
164 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
165 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
166 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
167 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
168 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
169 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
170 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
171 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
172 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
173 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
174 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
175 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
176 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
177 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
178 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
179 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
180 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
181 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
182 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
183 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
184 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
185 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
186 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
187 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
188 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
189 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
190 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
191 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
192 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
193 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
194 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
195 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
196 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 10.00% Type=B with end opened Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1' ' ' 1 2 4 10 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
197 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
198 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened Branch outage: 2 CLAYTOR 132.kV - 5 FIELDALE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'FIELDALE' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
199 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened Branch outage: 2 CLAYTOR 132.kV - 4 TENNESSEE 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'TENNESSEE' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
200 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened Branch outage: 2 CLAYTOR 132.kV - 1 GLEN LYN 132.kV 2L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'GLEN LYN' 132 1 '2' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
201 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened Branch outage: 6 NEVADA 132.kV - 0 BUS0 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'BUS0' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
202 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened Branch outage: 6 NEVADA 132.kV - 8 REUSENS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'REUSENS' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
203 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened Branch outage: 6 NEVADA 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'OHIO' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
204 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV - 0 DOT BUS 13.8kV 1X | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 10 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
205 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened Branch outage: 6 NEVADA 132.kV - 10 NEW HAMPSHR 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'NEVADA' 132 'NEW HAMPSHR' 33 2 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
206 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened Branch outage: 5 FIELDALE 132.kV - 7 OHIO 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'FIELDALE' 132 'OHIO' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
207 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened Branch outage: 4 TENNESSEE 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'TEXAS' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
208 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened Branch outage: 4 TENNESSEE 132.kV - 6 NEVADA 132.kV 1P | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'NEVADA' 132 3 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
209 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened Branch outage: 4 TENNESSEE 132.kV - 12 VERMONT 33.kV 1T | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'TENNESSEE' 132 'VERMONT' 33 2 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'
210 | Interm. Fault on: 6 NEVADA 132.kV - 2 CLAYTOR 132.kV 1L 1LG 15.00% Type=B with end opened Branch outage: 1 GLEN LYN 132.kV - 3 TEXAS 132.kV 1L | 0 1 0 0 0 0 0 0.4 0 0 | ' ' 0 0 8 0 0 0 0 0 0 0 0 0 'CLAYTOR' 132 'NEVADA' 132 1 '1' ' ' 0 0 5 0 0 0 0 0 0 0 0 0 'GLEN LYN' 132 'TEXAS' 132 1 '1' ' ' 1 2 4 15 0 0 0 0 0 0 0 0 'NEVADA' 132 'CLAYTOR' 132 1 '1'

## result
RELAY QUANTITIES REPORT
OLR FILE | C:\Program Files (x86)\ASPEN\1LPFv15\SAMPLE30_1.OLR
DATE | 2021-03-20 11:36:40
Fault No | Relay group | Relay ID | Relay Op. Qty (amps or ohm) | RelayTime (s) | IAmag | IAang | IBmag | IBang | Icmag | ICang | Vamag | VAang | VBmag | VBang | VCmag | VCang
1 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1203 | -80 | 1203 | 159 | 1203 | 39 | 43 | -6 | 43 | -126 | 43 | 113
1 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1203 | -80 | 1203 | 159 | 1203 | 39 | 43 | -6 | 43 | -126 | 43 | 113
2 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1162 | -80 | 1162 | 159 | 1162 | 39 | 41 | -7 | 41 | -127 | 41 | 112
2 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1162 | -80 | 1162 | 159 | 1162 | 39 | 41 | -7 | 41 | -127 | 41 | 112
3 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1361 | -79 | 1361 | 160 | 1361 | 40 | 49 | -5 | 49 | -125 | 49 | 114
3 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1361 | -79 | 1361 | 160 | 1361 | 40 | 49 | -5 | 49 | -125 | 49 | 114
4 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1166 | -80 | 1166 | 159 | 1166 | 39 | 41 | -6 | 41 | -126 | 41 | 113
4 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1166 | -80 | 1166 | 159 | 1166 | 39 | 41 | -6 | 41 | -126 | 41 | 113
5 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1204 | -80 | 1204 | 159 | 1204 | 39 | 43 | -6 | 43 | -126 | 43 | 113
5 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1204 | -80 | 1204 | 159 | 1204 | 39 | 43 | -6 | 43 | -126 | 43 | 113
6 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1204 | -80 | 1204 | 159 | 1204 | 39 | 43 | -6 | 43 | -126 | 43 | 113
6 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1204 | -80 | 1204 | 159 | 1204 | 39 | 43 | -6 | 43 | -126 | 43 | 113
7 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1282 | -79 | 1282 | 160 | 1282 | 40 | 46 | -5 | 46 | -125 | 46 | 114
7 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1282 | -79 | 1282 | 160 | 1282 | 40 | 46 | -5 | 46 | -125 | 46 | 114
8 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1203 | -80 | 1203 | 159 | 1203 | 39 | 43 | -6 | 43 | -126 | 43 | 113
8 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1203 | -80 | 1203 | 159 | 1203 | 39 | 43 | -6 | 43 | -126 | 43 | 113
9 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1206 | -80 | 1206 | 159 | 1206 | 39 | 43 | -6 | 43 | -126 | 43 | 113
9 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1206 | -80 | 1206 | 159 | 1206 | 39 | 43 | -6 | 43 | -126 | 43 | 113
10 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1282 | -79 | 1282 | 160 | 1282 | 40 | 46 | -5 | 46 | -125 | 46 | 114
10 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1282 | -79 | 1282 | 160 | 1282 | 40 | 46 | -5 | 46 | -125 | 46 | 114
11 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1292 | -79 | 1292 | 160 | 1292 | 40 | 46 | -6 | 46 | -126 | 46 | 113
11 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1292 | -79 | 1292 | 160 | 1292 | 40 | 46 | -6 | 46 | -126 | 46 | 113
12 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1528 | -77 | 1528 | 162 | 1528 | 42 | 54 | -4 | 54 | -124 | 54 | 115
12 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1528 | -77 | 1528 | 162 | 1528 | 42 | 54 | -4 | 54 | -124 | 54 | 115
13 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1178 | -80 | 1178 | 159 | 1178 | 39 | 42 | -6 | 42 | -126 | 42 | 113
13 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1178 | -80 | 1178 | 159 | 1178 | 39 | 42 | -6 | 42 | -126 | 42 | 113
14 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP3 | 1 | 1291 | -79 | 1291 | 160 | 1291 | 40 | 46 | -6 | 46 | -126 | 46 | 113
14 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1291 | -79 | 1291 | 160 | 1291 | 40 | 46 | -6 | 46 | -126 | 46 | 113
15 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1449 | -79 | 1449 | 160 | 1449 | 40 | 46 | -5 | 46 | -125 | 46 | 114
15 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1449 | -79 | 1449 | 160 | 1449 | 40 | 46 | -5 | 46 | -125 | 46 | 114
16 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1395 | -79 | 1395 | 160 | 1395 | 40 | 45 | -6 | 45 | -126 | 45 | 113
16 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1395 | -79 | 1395 | 160 | 1395 | 40 | 45 | -6 | 45 | -126 | 45 | 113
17 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1556 | -78 | 1556 | 161 | 1556 | 41 | 50 | -5 | 50 | -125 | 50 | 114
17 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1556 | -78 | 1556 | 161 | 1556 | 41 | 50 | -5 | 50 | -125 | 50 | 114
18 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1407 | -79 | 1407 | 160 | 1407 | 40 | 45 | -5 | 45 | -125 | 45 | 114
18 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1407 | -79 | 1407 | 160 | 1407 | 40 | 45 | -5 | 45 | -125 | 45 | 114
19 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1448 | -79 | 1448 | 160 | 1448 | 40 | 46 | -5 | 46 | -125 | 46 | 114
19 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1448 | -79 | 1448 | 160 | 1448 | 40 | 46 | -5 | 46 | -125 | 46 | 114
20 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1433 | -79 | 1433 | 160 | 1433 | 40 | 46 | -6 | 46 | -126 | 46 | 114
20 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1433 | -79 | 1433 | 160 | 1433 | 40 | 46 | -6 | 46 | -126 | 46 | 114
21 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1496 | -78 | 1496 | 161 | 1496 | 41 | 48 | -5 | 48 | -125 | 48 | 114
21 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1496 | -78 | 1496 | 161 | 1496 | 41 | 48 | -5 | 48 | -125 | 48 | 114
22 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1434 | -79 | 1434 | 160 | 1434 | 40 | 46 | -6 | 46 | -126 | 46 | 114
22 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1434 | -79 | 1434 | 160 | 1434 | 40 | 46 | -6 | 46 | -126 | 46 | 114
23 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1449 | -79 | 1449 | 160 | 1449 | 40 | 46 | -5 | 46 | -125 | 46 | 114
23 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1449 | -79 | 1449 | 160 | 1449 | 40 | 46 | -5 | 46 | -125 | 46 | 114
24 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1495 | -78 | 1495 | 161 | 1495 | 41 | 48 | -5 | 48 | -125 | 48 | 114
24 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1495 | -78 | 1495 | 161 | 1495 | 41 | 48 | -5 | 48 | -125 | 48 | 114
25 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1511 | -79 | 1511 | 160 | 1511 | 40 | 48 | -5 | 48 | -125 | 48 | 114
25 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1511 | -79 | 1511 | 160 | 1511 | 40 | 48 | -5 | 48 | -125 | 48 | 114
26 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1690 | -77 | 1690 | 162 | 1690 | 42 | 54 | -4 | 54 | -124 | 54 | 115
26 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1690 | -77 | 1690 | 162 | 1690 | 42 | 54 | -4 | 54 | -124 | 54 | 115
27 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1423 | -79 | 1423 | 160 | 1423 | 40 | 46 | -5 | 46 | -125 | 46 | 114
27 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1423 | -79 | 1423 | 160 | 1423 | 40 | 46 | -5 | 46 | -125 | 46 | 114
28 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1510 | -79 | 1510 | 160 | 1510 | 40 | 48 | -5 | 48 | -125 | 48 | 114
28 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1510 | -79 | 1510 | 160 | 1510 | 40 | 48 | -5 | 48 | -125 | 48 | 114
29 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1564 | -79 | 1564 | 160 | 1564 | 40 | 47 | -5 | 47 | -125 | 47 | 114
29 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1564 | -79 | 1564 | 160 | 1564 | 40 | 47 | -5 | 47 | -125 | 47 | 114
30 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1503 | -79 | 1503 | 160 | 1503 | 40 | 45 | -5 | 45 | -125 | 45 | 114
30 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1503 | -79 | 1503 | 160 | 1503 | 40 | 45 | -5 | 45 | -125 | 45 | 114
31 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1654 | -78 | 1654 | 161 | 1654 | 41 | 50 | -5 | 50 | -125 | 50 | 114
31 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1654 | -78 | 1654 | 161 | 1654 | 41 | 50 | -5 | 50 | -125 | 50 | 114
32 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1519 | -79 | 1519 | 160 | 1519 | 40 | 46 | -5 | 46 | -125 | 46 | 114
32 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1519 | -79 | 1519 | 160 | 1519 | 40 | 46 | -5 | 46 | -125 | 46 | 114
33 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1563 | -79 | 1563 | 160 | 1563 | 40 | 47 | -5 | 47 | -125 | 47 | 114
33 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1563 | -79 | 1563 | 160 | 1563 | 40 | 47 | -5 | 47 | -125 | 47 | 114
34 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1544 | -79 | 1544 | 160 | 1544 | 40 | 47 | -5 | 47 | -125 | 47 | 114
34 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1544 | -79 | 1544 | 160 | 1544 | 40 | 47 | -5 | 47 | -125 | 47 | 114
35 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1602 | -78 | 1602 | 161 | 1602 | 41 | 48 | -5 | 48 | -125 | 48 | 114
35 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1602 | -78 | 1602 | 161 | 1602 | 41 | 48 | -5 | 48 | -125 | 48 | 114
36 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1545 | -79 | 1545 | 160 | 1545 | 40 | 47 | -5 | 47 | -125 | 47 | 114
36 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1545 | -79 | 1545 | 160 | 1545 | 40 | 47 | -5 | 47 | -125 | 47 | 114
37 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1563 | -79 | 1563 | 160 | 1563 | 40 | 47 | -5 | 47 | -125 | 47 | 114
37 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1563 | -79 | 1563 | 160 | 1563 | 40 | 47 | -5 | 47 | -125 | 47 | 114
38 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1601 | -78 | 1601 | 161 | 1601 | 41 | 48 | -5 | 48 | -125 | 48 | 114
38 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1601 | -78 | 1601 | 161 | 1601 | 41 | 48 | -5 | 48 | -125 | 48 | 114
39 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1618 | -78 | 1618 | 161 | 1618 | 41 | 49 | -5 | 49 | -125 | 49 | 114
39 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1618 | -78 | 1618 | 161 | 1618 | 41 | 49 | -5 | 49 | -125 | 49 | 114
40 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1778 | -78 | 1778 | 162 | 1778 | 42 | 54 | -4 | 54 | -124 | 54 | 115
40 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1778 | -78 | 1778 | 162 | 1778 | 42 | 54 | -4 | 54 | -124 | 54 | 115
41 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1537 | -79 | 1537 | 160 | 1537 | 40 | 47 | -5 | 47 | -125 | 47 | 114
41 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1537 | -79 | 1537 | 160 | 1537 | 40 | 47 | -5 | 47 | -125 | 47 | 114
42 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | ZP2 | 0 | 1617 | -78 | 1617 | 161 | 1617 | 41 | 49 | -5 | 49 | -125 | 49 | 114
42 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 1617 | -78 | 1617 | 161 | 1617 | 41 | 49 | -5 | 49 | -125 | 49 | 114
43 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 115
43 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 115
44 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 116
44 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 116
45 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | -3 | 65 | -123 | 65 | 117
45 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | -3 | 65 | -123 | 65 | 117
46 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 115
46 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 115
47 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 115
47 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 115
48 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 115
48 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 115
49 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
49 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
50 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 115
50 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 115
51 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 115
51 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -4 | 58 | -124 | 58 | 115
52 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
52 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
53 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | -3 | 61 | -123 | 61 | 116
53 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | -3 | 61 | -123 | 61 | 116
54 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | -1 | 70 | -121 | 70 | 118
54 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | -1 | 70 | -121 | 70 | 118
55 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | -4 | 57 | -124 | 57 | 115
55 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | -4 | 57 | -124 | 57 | 115
56 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | -3 | 61 | -123 | 61 | 116
56 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | -3 | 61 | -123 | 61 | 116
57 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
57 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
58 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
58 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
59 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | -2 | 66 | -122 | 66 | 117
59 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | -2 | 66 | -122 | 66 | 117
60 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
60 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
61 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
61 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
62 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -3 | 59 | -123 | 59 | 116
62 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -3 | 59 | -123 | 59 | 116
63 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | -3 | 62 | -123 | 62 | 116
63 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | -3 | 62 | -123 | 62 | 116
64 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -3 | 59 | -123 | 59 | 116
64 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -3 | 59 | -123 | 59 | 116
65 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
65 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -3 | 60 | -123 | 60 | 116
66 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | -3 | 62 | -123 | 62 | 116
66 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | -3 | 62 | -123 | 62 | 116
67 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | -3 | 63 | -123 | 63 | 116
67 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | -3 | 63 | -123 | 63 | 116
68 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | -1 | 71 | -121 | 71 | 118
68 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | -1 | 71 | -121 | 71 | 118
69 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -3 | 59 | -123 | 59 | 116
69 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -3 | 59 | -123 | 59 | 116
70 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | -3 | 63 | -123 | 63 | 116
70 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | -3 | 63 | -123 | 63 | 116
71 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1180 | -78 | 105 | -98 | 47 | -146 | 42 | -5 | 78 | -121 | 77 | 121
71 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1299.87 | 0 | 1180 | -78 | 105 | -98 | 47 | -146 | 42 | -5 | 78 | -121 | 77 | 121
72 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1130 | -78 | 99 | -101 | 47 | -156 | 40 | -5 | 78 | -121 | 77 | 121
72 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1234.83 | 0 | 1130 | -78 | 99 | -101 | 47 | -156 | 40 | -5 | 78 | -121 | 77 | 121
73 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1301 | -79 | 56 | -129 | 54 | 160 | 46 | -5 | 78 | -122 | 77 | 122
73 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1313.01 | 0 | 1301 | -79 | 56 | -129 | 54 | 160 | 46 | -5 | 78 | -122 | 77 | 122
74 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1146 | -78 | 103 | -98 | 45 | -145 | 41 | -5 | 78 | -121 | 76 | 121
74 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1264.06 | 0 | 1146 | -78 | 103 | -98 | 45 | -145 | 41 | -5 | 78 | -121 | 76 | 121
75 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1181 | -78 | 104 | -98 | 45 | -148 | 42 | -5 | 78 | -121 | 77 | 121
75 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1297.68 | 0 | 1181 | -78 | 104 | -98 | 45 | -148 | 42 | -5 | 78 | -121 | 77 | 121
76 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1180 | -78 | 156 | -95 | 77 | -119 | 42 | -5 | 79 | -122 | 77 | 122
76 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1392.62 | 0 | 1180 | -78 | 156 | -95 | 77 | -119 | 42 | -5 | 79 | -122 | 77 | 122
77 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1266 | -77 | 138 | -94 | 58 | -132 | 45 | -3 | 78 | -121 | 77 | 121
77 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1435.57 | 0 | 1266 | -77 | 138 | -94 | 58 | -132 | 45 | -3 | 78 | -121 | 77 | 121
78 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1174 | -78 | 139 | -98 | 67 | -129 | 42 | -5 | 78 | -122 | 77 | 122
78 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1352.6 | 0 | 1174 | -78 | 139 | -98 | 67 | -129 | 42 | -5 | 78 | -122 | 77 | 122
79 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1183 | -78 | 107 | -98 | 48 | -146 | 42 | -5 | 78 | -121 | 77 | 121
79 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1305.65 | 0 | 1183 | -78 | 107 | -98 | 48 | -146 | 42 | -5 | 78 | -121 | 77 | 121
80 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1266 | -77 | 138 | -94 | 58 | -132 | 45 | -3 | 78 | -121 | 77 | 121
80 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1435.97 | 0 | 1266 | -77 | 138 | -94 | 58 | -132 | 45 | -3 | 78 | -121 | 77 | 121
81 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1281 | -77 | 107 | -84 | 40 | -100 | 46 | -4 | 77 | -121 | 77 | 120
81 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1427.04 | 0 | 1281 | -77 | 107 | -84 | 40 | -100 | 46 | -4 | 77 | -121 | 77 | 120
82 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1478 | -78 | 23 | 102 | 30 | 108 | 53 | -4 | 77 | -121 | 77 | 121
82 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1425.02 | 0 | 1478 | -78 | 23 | 102 | 30 | 108 | 53 | -4 | 77 | -121 | 77 | 121
83 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1164 | -78 | 94 | -97 | 44 | -147 | 41 | -5 | 78 | -120 | 76 | 121
83 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1271.76 | 0 | 1164 | -78 | 94 | -97 | 44 | -147 | 41 | -5 | 78 | -120 | 76 | 121
84 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1280 | -77 | 108 | -83 | 41 | -101 | 46 | -4 | 77 | -121 | 77 | 120
84 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1427.18 | 0 | 1280 | -77 | 108 | -83 | 41 | -101 | 46 | -4 | 77 | -121 | 77 | 120
85 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1412 | -78 | 89 | -100 | 41 | -176 | 45 | -4 | 78 | -121 | 77 | 121
85 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1492.05 | 0 | 1412 | -78 | 89 | -100 | 41 | -176 | 45 | -4 | 78 | -121 | 77 | 121
86 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1347 | -78 | 82 | -103 | 46 | 172 | 43 | -4 | 78 | -121 | 77 | 121
86 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1409.49 | 0 | 1347 | -78 | 82 | -103 | 46 | 172 | 43 | -4 | 78 | -121 | 77 | 121
87 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1496 | -78 | 50 | -124 | 50 | 153 | 48 | -5 | 78 | -121 | 77 | 121
87 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1503. | 0 | 1496 | -78 | 50 | -124 | 50 | 153 | 48 | -5 | 78 | -121 | 77 | 121
88 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1378 | -78 | 89 | -97 | 36 | -171 | 44 | -4 | 77 | -121 | 76 | 121
88 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1462.35 | 0 | 1378 | -78 | 89 | -97 | 36 | -171 | 44 | -4 | 77 | -121 | 76 | 121
89 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1412 | -78 | 88 | -100 | 40 | -178 | 45 | -4 | 78 | -121 | 77 | 121
89 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1489.45 | 0 | 1412 | -78 | 88 | -100 | 40 | -178 | 45 | -4 | 78 | -121 | 77 | 121
90 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1392 | -78 | 133 | -96 | 55 | -134 | 45 | -4 | 78 | -122 | 77 | 122
90 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1553.09 | 0 | 1392 | -78 | 133 | -96 | 55 | -134 | 45 | -4 | 78 | -122 | 77 | 122
91 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1466 | -77 | 119 | -95 | 44 | -155 | 47 | -4 | 78 | -121 | 77 | 121
91 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1591.35 | 0 | 1466 | -77 | 119 | -95 | 44 | -155 | 47 | -4 | 78 | -121 | 77 | 121
92 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1390 | -78 | 119 | -98 | 51 | -148 | 45 | -4 | 78 | -122 | 77 | 122
92 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1522.46 | 0 | 1390 | -78 | 119 | -98 | 51 | -148 | 45 | -4 | 78 | -122 | 77 | 122
93 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1413 | -78 | 91 | -100 | 42 | -175 | 45 | -4 | 78 | -121 | 77 | 121
93 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1495.3 | 0 | 1413 | -78 | 91 | -100 | 42 | -175 | 45 | -4 | 78 | -121 | 77 | 121
94 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1465 | -77 | 119 | -95 | 45 | -155 | 47 | -4 | 78 | -121 | 77 | 121
94 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1591.72 | 0 | 1465 | -77 | 119 | -95 | 45 | -155 | 47 | -4 | 78 | -121 | 77 | 121
95 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1485 | -77 | 86 | -87 | 21 | -138 | 48 | -4 | 77 | -121 | 77 | 121
95 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1582.04 | 0 | 1485 | -77 | 86 | -87 | 21 | -138 | 48 | -4 | 77 | -121 | 77 | 121
96 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1637 | -78 | 23 | 103 | 30 | 108 | 53 | -4 | 77 | -121 | 77 | 121
96 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1583.34 | 0 | 1637 | -78 | 23 | 103 | 30 | 108 | 53 | -4 | 77 | -121 | 77 | 121
97 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1395 | -78 | 80 | -99 | 40 | -178 | 45 | -4 | 77 | -120 | 76 | 121
97 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1464.99 | 0 | 1395 | -78 | 80 | -99 | 40 | -178 | 45 | -4 | 77 | -120 | 76 | 121
98 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1484 | -77 | 87 | -87 | 22 | -138 | 48 | -4 | 77 | -121 | 77 | 121
98 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1582.08 | 0 | 1484 | -77 | 87 | -87 | 22 | -138 | 48 | -4 | 77 | -121 | 77 | 121
99 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1522 | -78 | 83 | -101 | 42 | 172 | 46 | -4 | 78 | -121 | 77 | 121
99 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1587.39 | 0 | 1522 | -78 | 83 | -101 | 42 | 172 | 46 | -4 | 78 | -121 | 77 | 121
100 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1449 | -78 | 76 | -104 | 49 | 161 | 44 | -4 | 78 | -121 | 77 | 121
100 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1495.55 | 0 | 1449 | -78 | 76 | -104 | 49 | 161 | 44 | -4 | 78 | -121 | 77 | 121
101 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1593 | -78 | 48 | -122 | 49 | 150 | 48 | -5 | 78 | -121 | 77 | 121
101 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1597.75 | 0 | 1593 | -78 | 48 | -122 | 49 | 150 | 48 | -5 | 78 | -121 | 77 | 121
102 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1487 | -78 | 84 | -97 | 35 | 177 | 45 | -4 | 77 | -121 | 77 | 121
102 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1559.14 | 0 | 1487 | -78 | 84 | -97 | 35 | 177 | 45 | -4 | 77 | -121 | 77 | 121
103 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1522 | -78 | 82 | -101 | 42 | 170 | 46 | -4 | 77 | -121 | 77 | 121
103 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1584.69 | 0 | 1522 | -78 | 82 | -101 | 42 | 170 | 46 | -4 | 77 | -121 | 77 | 121
104 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1496 | -78 | 125 | -97 | 49 | -143 | 45 | -4 | 78 | -122 | 77 | 122
104 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1637.9 | 0 | 1496 | -78 | 125 | -97 | 49 | -143 | 45 | -4 | 78 | -122 | 77 | 122
105 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1566 | -77 | 112 | -95 | 42 | -167 | 47 | -4 | 78 | -121 | 77 | 121
105 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1674.92 | 0 | 1566 | -77 | 112 | -95 | 42 | -167 | 47 | -4 | 78 | -121 | 77 | 121
106 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1495 | -78 | 112 | -99 | 47 | -158 | 45 | -4 | 78 | -121 | 77 | 122
106 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1610.52 | 0 | 1495 | -78 | 112 | -99 | 47 | -158 | 45 | -4 | 78 | -121 | 77 | 122
107 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1522 | -78 | 85 | -100 | 43 | 173 | 46 | -4 | 78 | -121 | 77 | 121
107 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1589.88 | 0 | 1522 | -78 | 85 | -100 | 43 | 173 | 46 | -4 | 78 | -121 | 77 | 121
108 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1566 | -77 | 112 | -95 | 43 | -167 | 47 | -4 | 78 | -121 | 77 | 121
108 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1675.27 | 0 | 1566 | -77 | 112 | -95 | 43 | -167 | 47 | -4 | 78 | -121 | 77 | 121
109 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1586 | -77 | 78 | -90 | 20 | -165 | 48 | -4 | 77 | -121 | 77 | 121
109 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1664.76 | 0 | 1586 | -77 | 78 | -90 | 20 | -165 | 48 | -4 | 77 | -121 | 77 | 121
110 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1722 | -78 | 24 | 103 | 31 | 108 | 52 | -4 | 77 | -121 | 77 | 121
110 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1667.71 | 0 | 1722 | -78 | 24 | 103 | 31 | 108 | 52 | -4 | 77 | -121 | 77 | 121
111 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1505 | -78 | 74 | -100 | 41 | 170 | 46 | -4 | 77 | -120 | 76 | 121
111 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1560.45 | 0 | 1505 | -78 | 74 | -100 | 41 | 170 | 46 | -4 | 77 | -120 | 76 | 121
112 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 1585 | -77 | 79 | -89 | 21 | -163 | 48 | -4 | 77 | -121 | 77 | 121
112 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1664.76 | 0 | 1585 | -77 | 79 | -89 | 21 | -163 | 48 | -4 | 77 | -121 | 77 | 121
113 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -3 | 77 | -120 | 76 | 120
113 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -3 | 77 | -120 | 76 | 120
114 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -2 | 77 | -120 | 76 | 120
114 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -2 | 77 | -120 | 76 | 120
115 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | -3 | 78 | -120 | 76 | 121
115 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | -3 | 78 | -120 | 76 | 121
116 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | -3 | 77 | -120 | 76 | 121
116 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | -3 | 77 | -120 | 76 | 121
117 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -3 | 77 | -120 | 76 | 120
117 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -3 | 77 | -120 | 76 | 120
118 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | -3 | 78 | -120 | 76 | 121
118 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | -3 | 78 | -120 | 76 | 121
119 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -2 | 77 | -120 | 76 | 120
119 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -2 | 77 | -120 | 76 | 120
120 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | -3 | 77 | -120 | 76 | 121
120 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | -3 | 77 | -120 | 76 | 121
121 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -3 | 77 | -120 | 76 | 120
121 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | -3 | 77 | -120 | 76 | 120
122 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -2 | 77 | -120 | 76 | 120
122 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -2 | 77 | -120 | 76 | 120
123 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | -1 | 76 | -120 | 76 | 120
123 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | -1 | 76 | -120 | 76 | 120
124 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | -1 | 77 | -120 | 76 | 120
124 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | -1 | 77 | -120 | 76 | 120
125 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | -2 | 77 | -119 | 75 | 120
125 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | -2 | 77 | -119 | 75 | 120
126 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | -1 | 76 | -120 | 76 | 120
126 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | -1 | 76 | -120 | 76 | 120
127 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -2 | 77 | -120 | 76 | 120
127 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -2 | 77 | -120 | 76 | 120
128 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -2 | 77 | -119 | 76 | 120
128 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -2 | 77 | -119 | 76 | 120
129 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | -2 | 78 | -120 | 76 | 121
129 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | -2 | 78 | -120 | 76 | 121
130 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -3 | 77 | -120 | 76 | 121
130 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -3 | 77 | -120 | 76 | 121
131 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -2 | 77 | -120 | 76 | 120
131 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -2 | 77 | -120 | 76 | 120
132 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -2 | 77 | -120 | 76 | 121
132 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -2 | 77 | -120 | 76 | 121
133 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | -2 | 77 | -120 | 76 | 120
133 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | -2 | 77 | -120 | 76 | 120
134 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -2 | 77 | -120 | 76 | 121
134 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -2 | 77 | -120 | 76 | 121
135 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -2 | 77 | -120 | 76 | 120
135 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | -2 | 77 | -120 | 76 | 120
136 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | -2 | 77 | -120 | 76 | 120
136 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | -2 | 77 | -120 | 76 | 120
137 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | -1 | 76 | -119 | 76 | 120
137 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | -1 | 76 | -119 | 76 | 120
138 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | -1 | 77 | -120 | 76 | 120
138 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | -1 | 77 | -120 | 76 | 120
139 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -2 | 77 | -119 | 75 | 120
139 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | -2 | 77 | -119 | 75 | 120
140 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | -1 | 76 | -119 | 76 | 120
140 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | -1 | 76 | -119 | 76 | 120
141 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 47 | 93 | 1180 | 161 | 105 | 141 | 77 | 1 | 42 | -125 | 78 | 118
141 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1299.87 | 0 | 47 | 93 | 1180 | 161 | 105 | 141 | 77 | 1 | 42 | -125 | 78 | 118
142 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 47 | 83 | 1130 | 161 | 99 | 138 | 77 | 1 | 40 | -125 | 78 | 118
142 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1234.83 | 0 | 47 | 83 | 1130 | 161 | 99 | 138 | 77 | 1 | 40 | -125 | 78 | 118
143 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 54 | 40 | 1301 | 160 | 56 | 110 | 77 | 2 | 46 | -125 | 78 | 118
143 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1313.01 | 0 | 54 | 40 | 1301 | 160 | 56 | 110 | 77 | 2 | 46 | -125 | 78 | 118
144 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 45 | 94 | 1146 | 161 | 103 | 141 | 76 | 1 | 41 | -125 | 78 | 118
144 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1264.06 | 0 | 45 | 94 | 1146 | 161 | 103 | 141 | 76 | 1 | 41 | -125 | 78 | 118
145 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 45 | 92 | 1181 | 161 | 104 | 141 | 77 | 1 | 42 | -125 | 78 | 118
145 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1297.68 | 0 | 45 | 92 | 1181 | 161 | 104 | 141 | 77 | 1 | 42 | -125 | 78 | 118
146 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 77 | 120 | 1180 | 161 | 156 | 144 | 77 | 2 | 42 | -125 | 79 | 117
146 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1392.62 | 0 | 77 | 120 | 1180 | 161 | 156 | 144 | 77 | 2 | 42 | -125 | 79 | 117
147 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 58 | 107 | 1266 | 162 | 138 | 145 | 77 | 1 | 45 | -123 | 78 | 118
147 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1435.57 | 0 | 58 | 107 | 1266 | 162 | 138 | 145 | 77 | 1 | 45 | -123 | 78 | 118
148 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 67 | 110 | 1174 | 161 | 139 | 142 | 77 | 2 | 42 | -125 | 78 | 117
148 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1352.6 | 0 | 67 | 110 | 1174 | 161 | 139 | 142 | 77 | 2 | 42 | -125 | 78 | 117
149 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 48 | 93 | 1183 | 161 | 107 | 141 | 77 | 1 | 42 | -125 | 78 | 118
149 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1305.65 | 0 | 48 | 93 | 1183 | 161 | 107 | 141 | 77 | 1 | 42 | -125 | 78 | 118
150 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 58 | 107 | 1266 | 162 | 138 | 145 | 77 | 1 | 45 | -123 | 78 | 118
150 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1435.97 | 0 | 58 | 107 | 1266 | 162 | 138 | 145 | 77 | 1 | 45 | -123 | 78 | 118
151 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 40 | 139 | 1281 | 162 | 107 | 156 | 77 | 0 | 46 | -124 | 77 | 118
151 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1427.04 | 0 | 40 | 139 | 1281 | 162 | 107 | 156 | 77 | 0 | 46 | -124 | 77 | 118
152 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 30 | -11 | 1478 | 161 | 23 | -17 | 77 | 1 | 53 | -124 | 77 | 118
152 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1425.02 | 0 | 30 | -11 | 1478 | 161 | 23 | -17 | 77 | 1 | 53 | -124 | 77 | 118
153 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 44 | 92 | 1164 | 161 | 94 | 142 | 76 | 1 | 41 | -125 | 78 | 119
153 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1271.76 | 0 | 44 | 92 | 1164 | 161 | 94 | 142 | 76 | 1 | 41 | -125 | 78 | 119
154 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 41 | 138 | 1280 | 162 | 108 | 156 | 77 | 0 | 46 | -124 | 77 | 118
154 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1427.18 | 0 | 41 | 138 | 1280 | 162 | 108 | 156 | 77 | 0 | 46 | -124 | 77 | 118
155 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 41 | 63 | 1412 | 161 | 89 | 139 | 77 | 1 | 45 | -124 | 78 | 118
155 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1492.05 | 0 | 41 | 63 | 1412 | 161 | 89 | 139 | 77 | 1 | 45 | -124 | 78 | 118
156 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 46 | 52 | 1347 | 161 | 82 | 136 | 77 | 1 | 43 | -124 | 78 | 118
156 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1409.49 | 0 | 46 | 52 | 1347 | 161 | 82 | 136 | 77 | 1 | 43 | -124 | 78 | 118
157 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 50 | 33 | 1496 | 161 | 50 | 115 | 77 | 1 | 48 | -125 | 78 | 118
157 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1503. | 0 | 50 | 33 | 1496 | 161 | 50 | 115 | 77 | 1 | 48 | -125 | 78 | 118
158 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 36 | 68 | 1378 | 161 | 89 | 142 | 76 | 1 | 44 | -124 | 77 | 118
158 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1462.35 | 0 | 36 | 68 | 1378 | 161 | 89 | 142 | 76 | 1 | 44 | -124 | 77 | 118
159 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 40 | 61 | 1412 | 161 | 88 | 139 | 77 | 1 | 45 | -124 | 78 | 118
159 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1489.45 | 0 | 40 | 61 | 1412 | 161 | 88 | 139 | 77 | 1 | 45 | -124 | 78 | 118
160 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 55 | 105 | 1392 | 161 | 133 | 143 | 77 | 2 | 45 | -124 | 78 | 117
160 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1553.09 | 0 | 55 | 105 | 1392 | 161 | 133 | 143 | 77 | 2 | 45 | -124 | 78 | 117
161 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 44 | 84 | 1466 | 162 | 119 | 144 | 77 | 1 | 47 | -124 | 78 | 118
161 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1591.35 | 0 | 44 | 84 | 1466 | 162 | 119 | 144 | 77 | 1 | 47 | -124 | 78 | 118
162 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 51 | 91 | 1390 | 161 | 119 | 141 | 77 | 2 | 45 | -124 | 78 | 118
162 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1522.46 | 0 | 51 | 91 | 1390 | 161 | 119 | 141 | 77 | 2 | 45 | -124 | 78 | 118
163 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 42 | 64 | 1413 | 161 | 91 | 140 | 77 | 1 | 45 | -124 | 78 | 118
163 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1495.3 | 0 | 42 | 64 | 1413 | 161 | 91 | 140 | 77 | 1 | 45 | -124 | 78 | 118
164 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 45 | 84 | 1465 | 162 | 119 | 145 | 77 | 1 | 47 | -124 | 78 | 118
164 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1591.72 | 0 | 45 | 84 | 1465 | 162 | 119 | 145 | 77 | 1 | 47 | -124 | 78 | 118
165 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 21 | 102 | 1485 | 162 | 86 | 152 | 77 | 1 | 48 | -124 | 77 | 118
165 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1582.04 | 0 | 21 | 102 | 1485 | 162 | 86 | 152 | 77 | 1 | 48 | -124 | 77 | 118
166 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 30 | -11 | 1637 | 161 | 23 | -16 | 77 | 1 | 53 | -124 | 77 | 118
166 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1583.34 | 0 | 30 | -11 | 1637 | 161 | 23 | -16 | 77 | 1 | 53 | -124 | 77 | 118
167 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 40 | 61 | 1395 | 161 | 80 | 140 | 76 | 1 | 45 | -124 | 77 | 119
167 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1464.99 | 0 | 40 | 61 | 1395 | 161 | 80 | 140 | 76 | 1 | 45 | -124 | 77 | 119
168 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 22 | 101 | 1484 | 162 | 87 | 152 | 77 | 1 | 48 | -124 | 77 | 118
168 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1582.08 | 0 | 22 | 101 | 1484 | 162 | 87 | 152 | 77 | 1 | 48 | -124 | 77 | 118
169 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 42 | 52 | 1522 | 161 | 83 | 138 | 77 | 1 | 46 | -124 | 78 | 118
169 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1587.39 | 0 | 42 | 52 | 1522 | 161 | 83 | 138 | 77 | 1 | 46 | -124 | 78 | 118
170 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 49 | 41 | 1449 | 161 | 76 | 135 | 77 | 1 | 44 | -124 | 78 | 118
170 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1495.55 | 0 | 49 | 41 | 1449 | 161 | 76 | 135 | 77 | 1 | 44 | -124 | 78 | 118
171 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 49 | 30 | 1593 | 161 | 48 | 117 | 77 | 1 | 48 | -125 | 78 | 118
171 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1597.75 | 0 | 49 | 30 | 1593 | 161 | 48 | 117 | 77 | 1 | 48 | -125 | 78 | 118
172 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 35 | 57 | 1487 | 161 | 84 | 142 | 77 | 1 | 45 | -124 | 77 | 118
172 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1559.14 | 0 | 35 | 57 | 1487 | 161 | 84 | 142 | 77 | 1 | 45 | -124 | 77 | 118
173 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 42 | 50 | 1522 | 161 | 82 | 138 | 77 | 1 | 46 | -124 | 77 | 118
173 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1584.69 | 0 | 42 | 50 | 1522 | 161 | 82 | 138 | 77 | 1 | 46 | -124 | 77 | 118
174 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 49 | 96 | 1496 | 161 | 125 | 143 | 77 | 2 | 45 | -124 | 78 | 118
174 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1637.9 | 0 | 49 | 96 | 1496 | 161 | 125 | 143 | 77 | 2 | 45 | -124 | 78 | 118
175 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 42 | 72 | 1566 | 162 | 112 | 144 | 77 | 1 | 47 | -124 | 78 | 118
175 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1674.92 | 0 | 42 | 72 | 1566 | 162 | 112 | 144 | 77 | 1 | 47 | -124 | 78 | 118
176 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 47 | 81 | 1495 | 161 | 112 | 140 | 77 | 2 | 45 | -124 | 78 | 118
176 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1610.52 | 0 | 47 | 81 | 1495 | 161 | 112 | 140 | 77 | 2 | 45 | -124 | 78 | 118
177 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 43 | 53 | 1522 | 161 | 85 | 139 | 77 | 1 | 46 | -124 | 78 | 118
177 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1589.88 | 0 | 43 | 53 | 1522 | 161 | 85 | 139 | 77 | 1 | 46 | -124 | 78 | 118
178 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 43 | 72 | 1566 | 162 | 112 | 144 | 77 | 1 | 47 | -124 | 78 | 118
178 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1675.27 | 0 | 43 | 72 | 1566 | 162 | 112 | 144 | 77 | 1 | 47 | -124 | 78 | 118
179 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 20 | 75 | 1586 | 162 | 78 | 150 | 77 | 1 | 48 | -124 | 77 | 118
179 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1664.76 | 0 | 20 | 75 | 1586 | 162 | 78 | 150 | 77 | 1 | 48 | -124 | 77 | 118
180 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 31 | -11 | 1722 | 161 | 24 | -16 | 77 | 1 | 52 | -124 | 77 | 118
180 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1667.71 | 0 | 31 | -11 | 1722 | 161 | 24 | -16 | 77 | 1 | 52 | -124 | 77 | 118
181 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 41 | 50 | 1505 | 161 | 74 | 139 | 76 | 1 | 46 | -124 | 77 | 119
181 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1560.45 | 0 | 41 | 50 | 1505 | 161 | 74 | 139 | 76 | 1 | 46 | -124 | 77 | 119
182 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 21 | 76 | 1585 | 162 | 79 | 150 | 77 | 1 | 48 | -124 | 77 | 118
182 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | TOC=1664.76 | 0 | 21 | 76 | 1585 | 162 | 79 | 150 | 77 | 1 | 48 | -124 | 77 | 118
183 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 58 | -123 | 77 | 119
183 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 58 | -123 | 77 | 119
184 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 58 | -122 | 77 | 120
184 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 58 | -122 | 77 | 120
185 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 63 | -123 | 78 | 119
185 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 63 | -123 | 78 | 119
186 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 57 | -123 | 77 | 119
186 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 57 | -123 | 77 | 119
187 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 58 | -123 | 77 | 119
187 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 58 | -123 | 77 | 119
188 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 57 | -123 | 78 | 119
188 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 57 | -123 | 78 | 119
189 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 60 | -122 | 77 | 119
189 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 60 | -122 | 77 | 119
190 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 57 | -123 | 77 | 119
190 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 57 | -123 | 77 | 119
191 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 58 | -123 | 77 | 119
191 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 58 | -123 | 77 | 119
192 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 60 | -122 | 77 | 119
192 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 60 | -122 | 77 | 119
193 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 62 | -121 | 76 | 120
193 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 62 | -121 | 76 | 120
194 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 70 | -121 | 77 | 119
194 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 70 | -121 | 77 | 119
195 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 57 | -122 | 77 | 120
195 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 57 | -122 | 77 | 120
196 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 62 | -121 | 76 | 120
196 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 62 | -121 | 76 | 120
197 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 60 | -122 | 77 | 119
197 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 60 | -122 | 77 | 119
198 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 60 | -122 | 77 | 120
198 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 60 | -122 | 77 | 120
199 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 64 | -122 | 78 | 119
199 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 64 | -122 | 78 | 119
200 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 59 | -123 | 77 | 119
200 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 59 | -123 | 77 | 119
201 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 60 | -122 | 77 | 119
201 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 60 | -122 | 77 | 119
202 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 59 | -122 | 77 | 119
202 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 59 | -122 | 77 | 119
203 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 62 | -122 | 77 | 120
203 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 62 | -122 | 77 | 120
204 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 59 | -122 | 77 | 119
204 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 1 | 59 | -122 | 77 | 119
205 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 60 | -122 | 77 | 119
205 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 60 | -122 | 77 | 119
206 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 62 | -122 | 77 | 120
206 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 62 | -122 | 77 | 120
207 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 63 | -121 | 76 | 120
207 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 63 | -121 | 76 | 120
208 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 70 | -121 | 77 | 119
208 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 70 | -121 | 77 | 119
209 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 59 | -122 | 77 | 120
209 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 59 | -122 | 77 | 120
210 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CLPhase2 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 63 | -121 | 76 | 120
210 | 2 CLAYTOR 132.kV - 6 NEVADA 132.kV 1 L Clav/Nev | CL-G1 | NOP | 9999 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 63 | -121 | 76 | 120